## Scenes
Scene 0 - Overall Scene
Scene 1 - PPE Tables in Yard
Scene 2 - Power Pole in Yard

## Script
SCRIPT
CLIENT |  |  |  | Conestoga College
PROJECT NAME |  |  |  | Powerline Module 5: Rubber / Polyethylene Protective Equipment Practical Application (Procedural)
PROJECT MANAGER |  |  |  | Christina Ly
VERSION CONTROL
REVISION |  | DATE | TYPE | COLOUR | EDITOR | VERSION CHANGES
0 |  | 2024-02-26 | Draft | Text | Ali Mouawieh, Christina Ly, & Jessica Scandaliato | Original Script
1 |  | 2024-05-10 | Draft | Text | Brad Naylor | Changes made by Conestoga
1 |  | 2024-05-14 | Draft | Text | Corey Berry | Changes made by Conestoga
2 |  | 2024-05-16 | Final | Text | Christina Ly | Cleaned up Conestoga edits and added changes across all modules.
CHARACTERS
NO. | CHARACTER |  | DESCRIPTION
1. | Narrator |  | Delivers commentary to convey the story and provides the Player guidance to complete task(s).
2. | Player |  | Conestoga student controlling the actions of the Powerline Technician (PLT) in the simulation for training purposes.
SCENES
NO. | SCENE |  |  | DESCRIPTION
0 | Overall |  |  | On a municipal roadway in a bucket truck servicing an overhead three-phase high-voltage electrical power pole.
1 | Road Phase |  |  | Powerline with conductors and half of the crossarm that is closest in proximity to the road. The Player will see an enclosed yard in the background when working on this phase.
INTRODUCTION
NO. | SCENE | CHARACTER | DIALOGUE |  |  |  | POP-UP PROMPTS | COMMENTS
1 | 1 | Narrator | Please ensure you stay in fullscreen mode to have access to the full range of gameplay and visual settings. |  |  |  | N/A | A delay will be added before the next narration lines are fed to allow Learner to put simulation in fullscreen mode.
2 | 1 | Narrator | Welcome to Module 5! In this module, you will apply the skills from Module 4 to install rubber protective equipment as a physical barrier and work according to the Safe Limits of Approach to replace a dead-end insulator on the road phase of an underbuild circuit. The voltage on the circuit is 8/13.8kv, so be sure to adhere to the Limits of Approach for that voltage level. |  |  |  | N/A
TUTORIAL
NO. | SCENE | CHARACTER | DIALOGUE |  |  |  | POP-UP PROMPTS | COMMENTS
3 | 1 | Narrator | Before we get started, let's do a quick run-through of the gaming controls you learned in Module 4. Use the keyboard keys W, A, S, and D to move the bucket forward, backward, left, and right. |  |  |  | Helpful Hint: Click the "W," "A," "S," and "D" keyboard keys to move the bucket in different directions.
4 | 1 | Narrator | Great! Now, move the bucket up and down by clicking the spacebar and the left-shift keyboard keys. |  |  |  | Helpful Hint: Move the bucket up and down by pressing the spacebar and left shift keyboard keys.
5 | 1 | Narrator | If you forget the gaming controls at any point, press the "P" keyboard key and select "Controls" in the Pause Menu to view the keyboard legend. |  |  |  | N/A
6 | 1 | Narrator | Remember to always be vigilant of your Safe Limits of Approach. You can refer to these limits throughout the module at the top of the screen. |  |  |  | N/A
7 | 1 | Narrator | You are now ready to install rubber protective equipment and set up the rigging and live line tools required to replace the road phase dead-end insulator. Let's begin! |  |  |  | N/A
PART 1 - INSTALLING RUBBER BARRIER AND SET-UP RIGGING
NO. | SCENE | CHARACTER | DIALOGUE |  |  |  | POP-UP PROMPTS | COMMENTS
8 | 1 | Narrator | Start with installing the rubber hoses on the road phase powerline. Approach the center of the blue shadow. |  |  |  | Helpful Hint: Use movement keys (WASD, space bar, and left shift) to navigate to the blue shadow on the powerline. | Ensure Learner is at blue field before next narration line is fed.
9 | 1 | Narrator | Select the rubber hose in the bucket by using the mouse to hover over it until it lights up blue. Click the left mouse button to select and pick up the rubber hose. |  |  |  | Helpful Hint: Use the mouse to hover over the appropriate item. When it lights up blue, click the left mouse button to select the item. | Learner will be blocked from picking up any other item except the insulating hose here. The rest of the simulation, the Learner will be able to select incorrect items.
10 | 1 | Narrator | Use the crosshair controlled by the mouse to move the rubber hose to the blue shadow on the powerline. |  |  |  | Helpful Hint: Drag the selected item to the blue shadow.
11 | 1 | Narrator | Repeat the same steps to install the next two pieces of rubber hoses. |  |  |  | Helpful Hint: Use the mouse to hover over the appropriate item. When it lights up blue, click the left mouse button to select the item and drag it to the blue shadow. Alert: You have selected the incorrect item. Click the left mouse button to drop the item and try again with a new selection.
12 | 1 | Narrator | Great work! The rubber hoses are now installed, effectively covering your first point of contact. Next, make your way to the blue shadow and select the rubber protective equipment that is best suited to effectively cover the gradient voltage across the dead-end insulator. |  |  |  | Helpful Hint: Use the mouse to hover over the appropriate item. When it lights up blue, click the left mouse button to select the item and drag it to the blue shadow. Alert: You are working at an unsafe distance. Review the distances on the top of your screen and reposition yourself to a safe working distance using movement keys (WASD, space bar, and left shift). Alert: You have selected the incorrect item. Click the left mouse button to drop the item and try again with a new selection. | If the Learner is at an unsafe working distance and selects the incorrect rubber protective equipment, the unsafe distance alert will appear first. Once repositioned to a safe working distance, then the incorrect item alert will appear.
13 | 1 | Narrator | Use rubber clamp pins to secure the solid rubber blanket and prevent it from shifting or moving. This avoids accidental exposure to high-voltage areas. Remember to work according to the Safe Limits of Approach! |  |  |  | Helpful Hint: Use the mouse to hover over the appropriate item. When it lights up blue, click the left mouse button to select the item and drag it to the blue shadow. Alert: You have selected the incorrect item. Click the left mouse button to drop the item and try again with a new selection.
14 | 1 | Narrator | Nice job! We can now begin setting up the rigging and live line tools. Move towards the center of the road phase crossarm. |  |  |  | Helpful Hint: Use movement keys (WASD, space bar, and left shift) to navigate to the road phase crossarm. | Ensure Learner is at crossarm before next narration line is fed.
15 | 1 | Narrator | You will see three yellow slings with different distances in inches from the crossarm bolt wrapped around the crossarm in front of you. Select the best position to install the yellow sling by hovering over it until it lights up blue and clicking the left mouse button. Be sure to maintain at least 6" to any covered energized apparatus, and at least 1' to any uncovered energized apparatus! |  |  |  | Helpful Hint: Use your mouse to hover over the yellow sling at the correct distance. When it lights up blue, click the left mouse button to install it. Alert: That's incorrect! You're trying to attach the yellow sling at a non-optimal distance from the corner of the crossarm. Please try again.
16 | 1 | Narrator | That's correct! The sling should be installed 6" away from the end of the crossarm. This distance is far enough away from the road phase that your rigging will not bind on the conductor or insulator, but not so far away that the tension of the rigging will pull the insulator away from its connection points, which would make removal and reinstallation more difficult. |  |  |  | N/A
17 | 1 | Narrator | Attach the spiral link stick to the end of the yellow sling. For this training module, the yellow sling is hanging horizontally, so you are able to visually see the proper positioning of the yellow sling and link stick. In the field, the yellow sling will hang vertically for the PLT to easily install the link stick, not horizontally. |  |  |  | Helpful Hint: Use the mouse to hover over the appropriate item. When it lights up blue, click the left mouse button to select the item and drag it to the blue shadow. Alert: You have selected the incorrect item. Click the left mouse button to drop the item and try again with a new selection.
18 | 1 | Narrator | The insulated portion of the spiral link stick should be aligned with the insulator. Look to the bottom left of the screen for a visual guide. You will see that the solid rubber blanket covering the insulator is translucent, so you can easily see how the link stick should align with the insulator. If the sling is too long, the voltage tracking across the insulator could contact and flow through the sling, causing the sling to burn and drop the energized conductor to the ground. |  |  |  | N/A
19 | 1 | Narrator | Let's now cover the crossarm with rubber. Find the appropriate rubber protective equipment to cover the area of the crossarm with the yellow sling. |  |  |  | Helpful Hint: Use the mouse to hover over the appropriate item. When it lights up blue, click the left mouse button to select the item and drag it to the blue shadow. Alert: You have selected the incorrect item. Click the left mouse button to drop the item and try again with a new selection.
20 | 1 | Narrator | Great choice! The split rubber blanket has an opening that makes the yellow sling and spiral link stick accessible. Don't forget the rubber clamps to hold the blanket in place. |  |  |  | Helpful Hint: Use the mouse to hover over the appropriate item. When it lights up blue, click the left mouse button to select the item and drag it to the blue shadow. Alert: You have selected the incorrect item. Click the left mouse button to drop the item and try again with a new selection.
21 | 1 | Narrator | Now, place the insulator hood on the corner to finish insulating the crossarm. |  |  |  | Helpful Hint: Use the mouse to hover over the appropriate item. When it lights up blue, click the left mouse button to select the item and drag it to the blue shadow. Alert: You have selected the incorrect item. Click the left mouse button to drop the item and try again with a new selection.
22 | 1 | Narrator | Let's continue to set up the rigging. Move toward the blue shadow visible between the rubber hoses you placed on the road phase powerline earlier in this module. |  |  |  | Helpful Hint: Use movement keys (WASD, space bar, and left shift) to navigate to the blue shadow on the powerline. | Add 9 second delay to allow Learner to get into position.
23 | 1 | Narrator | A space between the rubber hoses will need to be opened to make room for the conductor grip. Click on the blue box with your mouse to create the space needed to install the grip. |  |  |  | Helpful Hint: Click the left mouse button on the blue box between the two rubber hoses.
24 | 1 | Narrator | Select the wire pulling grip from your bucket and install it onto the opening you made between the rubber hoses. |  |  |  | Helpful Hint: Use the mouse to hover over the appropriate item. When it lights up blue, click the left mouse button to select the item and drag it to the blue shadow. Alert: You have selected the incorrect item. Click the left mouse button to drop the item and try again with a new selection.
25 | 1 | Narrator | Great! You're now ready to attach the nylon ratchet tensioner, also known as a web hoist. Select it from the bucket and move it to the blue shadow above the powerline. |  |  |  | Helpful Hint: Use the mouse to hover over the appropriate item. When it lights up blue, click the left mouse button to select the item and drag it to the blue shadow. Alert: You have selected the incorrect item. Click the left mouse button to drop the item and try again with a new selection.
26 | 1 | Narrator | You will see that the web hoist has an upper and lower hook highlighted in green. Click on the correct hook that needs to be fastened to the conductor grip. |  |  |  | Helpful Hint: Use the left mouse button to click on the correct green hook to fasten it to the grip. Alert: That's incorrect! Attaching the lower hook to the grip are both less efficient and less safe. Please try again.
27 | 1 | Narrator | That's correct! The upper hook of the web hoist belongs on the wire grip. We have gone ahead and attached the lower hook to the spiral link stick and tensioned it for you. This orientation places the hoist body at the conductor grip and away from the area in which the work of replacing the insulator will be completed, creating less second-point-of-contact hazards in that area. |  |  |  | N/A
28 | 1 | Narrator | Cover the conductor grip and web hoist frame with a solid rubber blanket, as they may be within your safe limits of approach when working on the cross-arm to replace the insulator. |  |  |  | Helpful Hint: Use the mouse to hover over the appropriate item. When it lights up blue, click the left mouse button to select the item and drag it to the blue shadow. Alert: You have selected the incorrect item. Click the left mouse button to drop the item and try again with a new selection.
29 | 1 | Narrator | Remember to add rubber clamps on both sides of the blanket to keep them in place! |  |  |  | Helpful Hint: Use the mouse to hover over the appropriate item. When it lights up blue, click the left mouse button to select the item and drag it to the blue shadow. Alert: You have selected the incorrect item. Click the left mouse button to drop the item and try again with a new selection.
30 | 1 | Narrator | A commonly missed step in the field is securing the conductor to prevent it from swinging when disconnected from the insulator. Move the bucket to the left and fasten a gear tie to secure the conductor to the hoist webbing. |  |  |  | Helpful Hint: Use the mouse to hover over the appropriate item. When it lights up blue, click the left mouse button to select the item and drag it to the blue shadow. Alert: You have selected the incorrect item. Click the left mouse button to drop the item and try again with a new selection.
31 | 1 | Narrator | Now that the conductor is secured, select the appropriate rubber protective equipment to cover the spiral link stick and exposed hoist webbing to protect you from accidentally contacting them while you work to remove the insulator. |  |  |  | Helpful Hint: Use the mouse to hover over the appropriate item. When it lights up blue, click the left mouse button to select the item and drag it to the blue shadow. Alert: You have selected the incorrect item. Click the left mouse button to drop the item and try again with a new selection.
32 | 1 | Narrator | Great choice! The solid rubber blanket covers a large area without creating gaps that could expose the PLT to electrical hazards. As usual, secure the blanket with the rubber clamps. |  |  |  | Helpful Hint: Use the mouse to hover over the appropriate item. When it lights up blue, click the left mouse button to select the item and drag it to the blue shadow. Alert: You have selected the incorrect item. Click the left mouse button to drop the item and try again with a new selection.
PART 2 - REPLACING THE INSULATOR
NO. | SCENE | CHARACTER | DIALOGUE |  |  |  | POP-UP PROMPTS | COMMENTS
33 | 1 | Narrator | Now that the working area is insulated and the rigging has been set up, the next few steps will be to gain access to the road phase insulator to remove and replace it with a new one. Start by removing the rubber hood at the corner of the crossarm by hovering over it and clicking on it when it turns blue. |  |  |  | Helpful Hint: Use the mouse to hover over the rubber hood. When it lights up blue, click the left mouse button to remove it.
34 | 1 | Narrator | Next, remove the rubber clamps that are secured on the solid rubber blanket covering the road phase insulator. |  |  |  | Helpful Hint: Use the mouse to hover over the rubber clamps that are secured on the solid rubber blanket on the road phase insulator. When it lights up blue, click the left mouse button to remove it.
35 | 1 | Narrator | Go ahead and remove the solid rubber blanket to expose the insulator. Be mindful of your safe working limits here as you will be working closely to two exposed potentials! |  |  |  | Helpful Hint: Use the mouse to hover over the solid rubber blanket. When it lights up blue, click the left mouse button to remove it. Alert: You are working at an unsafe distance. Review the limits on the top of your screen and reposition yourself to a safe working distance using movement keys (WASD, space bar, and left shift).
36 | 1 | Narrator | You now have access to the old insulator and can begin removing it. You will see that the connection points on both ends of the insulator are highlighted in green. Select the green connection point that would be the safest to disconnect first. Be sure to maximize your Safe Limits to other potentials when making this disconnection. |  |  |  | Helpful Hint: Use the mouse to click on the green connection point that should be disconnected first. Alert: It is unsafe to disconnect the crossarm end first. Please try again.
37 | 1 | Narrator | Excellent choice! You've correctly identified that the conductor end of the insulator should be disconnected first. It is less safe to disconnect the crossarm end of the insulator first as the old insulator may be defective and leaking voltage, causing a difference of potential between the crossarm and the insulator when it is disconnected. |  |  |  | N/A
38 | 1 | Narrator | You'll see the road phase conductor dead-end clamp is hanging loose. It is important not to leave it exposed as it poses a second-point of contact hazard. Click on the green highlighted rubber blanket to tuck the conductor and dead-end clamp under it. |  |  |  | Helpful Hint: Use the mouse to click on the green highlighted solid rubber blanket.
39 | 1 | Narrator | It is now safe to remove the insulator from the crossarm connection. Position yourself to maximize your Safe Limits to any other potentials. |  |  |  | Helpful Hint: Use the mouse to hover over the insulator. When it lights up blue, click the left mouse button to remove it.
40 | 1 | Narrator | You can now install the new insulator. First, pick it up from the bucket and attach it to the crossarm. |  |  |  | Helpful Hint: Use the mouse to hover over the appropriate item. When it lights up blue, click the left mouse button to select the item and drag it to the blue shadow. Alert: You have selected the incorrect item. Click the left mouse button to drop the item and try again with a new selection.
41 | 1 | Narrator | To complete the installation, remove the conductor from under the solid rubber blanket it was originally tucked under. Click on the blanket behind the insulator to untuck it. Maximize your Safe Limits to the second-point of contact hazard created by the uncovered end of the crossarm. |  |  |  | Helpful Hint: Use the mouse to click on the green highlighted solid rubber blanket.
42 | 1 | Narrator | Great work! With the new insulator successfully installed, the final steps will be removing the rubber protective equipment and live line tools from the powerline. |  |  |  | N/A
PART 2 - REMOVING RUBBER BARRIER AND RIGGING
NO. | SCENE | CHARACTER | DIALOGUE |  |  |  | POP-UP PROMPTS | COMMENTS
43 | 1 | Narrator | To safely remove the live line tools, all exposed areas of the road phase powerline will need to be covered. Start by covering the newly installed insulator with the appropriate rubber protective equipment. |  |  |  | Helpful Hint: Use the mouse to hover over the appropriate item. When it lights up blue, click the left mouse button to select the item and drag it to the blue shadow. Alert: You have selected the incorrect item. Click the left mouse button to drop the item and try again with a new selection. Alert: You are working at an unsafe distance. Review the limits on the top of your screen and reposition yourself to a safe working distance using movement keys (WASD, space bar, and left shift).
44 | 1 | Narrator | The solid rubber blanket is correct! As usual, place the clamps on the blanket to secure it. |  |  |  | Helpful Hint: Use the mouse to hover over the appropriate item. When it lights up blue, click the left mouse button to select the item and drag it to the blue shadow. Alert: You have selected the incorrect item. Click the left mouse button to drop the item and try again with a new selection.
45 | 1 | Narrator | Next, move to the corner of the crossarm and cover it with the insulator hood. |  |  |  | Helpful Hint: Use the mouse to hover over the appropriate item. When it lights up blue, click the left mouse button to select the item and drag it to the blue shadow. Alert: You have selected the incorrect item. Click the left mouse button to drop the item and try again with a new selection.
46 | 1 | Narrator | Remove the gear tie to unsecure the road phase conductor from the ratchet hoist webbing. |  |  |  | Helpful Hint: Use the mouse to hover over the gear tie. When it lights up blue, click the left mouse button to remove it.
47 | 1 | Narrator | Position yourself to access the rubber clamps and solid rubber blanket located behind the road phase insulator. Remove both rubber clamps. |  |  |  | Helpful Hint: Use the mouse to hover over the rubber clamps behind the road phase insulator. When it lights up blue, click the left mouse button to remove it.
48 | 1 | Narrator | Now you can take off the solid rubber blanket covering the link stick and hoist webbing. |  |  |  | Helpful Hint: Use the mouse to hover over the solid rubber blanket that is covering the hoist webbing. When it lights up blue, click the left mouse button to remove it.
49 | 1 | Narrator | You're doing great! Now, move towards the solid rubber blanket that is currently draped over the conductor grip and web hoist. Remove the two rubber clamps. |  |  |  | Helpful Hint: Use the mouse to hover over the rubber clamps that are on the blanket, grip, and web hoist. When it lights up blue, click the left mouse button to remove it.
50 | 1 | Narrator | Go ahead and pull the rubber blanket off of the hoist and grip. |  |  |  | Helpful Hint: Use the mouse to hover over the rubber blanket. When it lights up blue, click the left mouse button to remove it.
51 | 1 | Narrator | Nice job! You are now ready to take off the web hoist. In the field, you would unhook the hoist from the grip and tighten the webbing while moving the bucket towards the spiral link stick. You would then unhook the webbing from the sprial link stick to complete removing the hoist. Click on the hoist and we will complete this step for you. |  |  |  | Helpful Hint: Use the mouse to hover over the hoist. When it lights up blue, click the left mouse button to remove it.
52 | 1 | Narrator | Next, remove the grip. |  |  |  | Helpful Hint: Use the mouse to hover over the grip. When it lights up blue, click the left mouse button to remove it.
53 | 1 | Narrator | Proceed to the crossarm to begin removing the rubber protective barriers. Begin by pulling off the insulator hood. |  |  |  | Helpful Hint: Use the mouse to hover over the insulator hood. When it lights up blue, click the left mouse button to remove it.
54 | 1 | Narrator | Next, unclip the rubber clamps that are currently securing the split rubber blanket on the crossarm. |  |  |  | Helpful Hint: Use the mouse to hover over the rubber clamps that are on the split blanket. When it lights up blue, click the left mouse button to remove it. Alert: You are working at an unsafe distance. Review the limits on the top of your screen and reposition yourself to a safe working distance using movement keys (WASD, space bar, and left shift).
55 | 1 | Narrator | Proceed to take off the split rubber blanket, so only the yellow sling and spiral link stick remains. |  |  |  | Helpful Hint: Use the mouse to hover over the split rubber blanket. When it lights up blue, click the left mouse button to remove it.
56 | 1 | Narrator | Detach the spiral link stick from the yellow sling. |  |  |  | Helpful Hint: Use the mouse to hover over the spiral link stick. When it lights up blue, click the left mouse button to remove it.
57 | 1 | Narrator | Untie the yellow sling from the crossarm. |  |  |  | Helpful Hint: Use the mouse to hover over the yellow sling. When it lights up blue, click the left mouse button to remove it.
58 | 1 | Narrator | You're almost done! Move to the insulator to start removing the rubber protective equipment. Begin by unclipping the clamps. |  |  |  | Helpful Hint: Use the mouse to hover over the rubber clamps. When it lights up blue, click the left mouse button to remove it.
59 | 1 | Narrator | Then, take off the rubber blanket to expose the road phase insulator. Remember your safe working limits at this step! Be mindful to keep a safe distance and not to bridge across different potentials. |  |  |  | Helpful Hint: Use the mouse to hover over the rubber blanket. When it lights up blue, click the left mouse button to remove it.
60 | 1 | Narrator | Only three rubber hoses remain to complete the job. Go ahead and remove them from the powerline. |  |  |  | Helpful Hint: Use the mouse to hover over the rubber hoses. When it lights up blue, click the left mouse button to remove it.
61 | 1 | Narrator | Congratulations! You safely removed all rubber equipment and live line tools from the powerline and have now completed Module 5. |  |  |  | N/A
62 | 1 | Narrator | Please download your certificate by clicking the "Download Certificate" button at the top right of your screen. |  |  |  | Helpful Hint: Click on the "Download Certificate" button to download your completion certificate. You can find your certificate in your computer's downloads folder.
63 | 1 | Narrator | Please exit out of the experience by hitting "ESC" on your keyboard. |  |  |  | Helpful Hint: Hit "ESC" on keyboard to exit the experience.

## Sheet1
fix script - so first hose, we tell them to pick up hose - ali implements
fix script for order of alerts
fix the script to combine alert with helpful hint - ali implements
blanket text on conductor - ali
helpful hints that are timed - make longer - double it
subtitles longer
christina to communicate to corey and brad not to do the step until the subtitles are done.
end of Monday. Send the script.